## Sheet1 (2)
Power supply and local control system for LED street Light load with Local and centralised Remote control facility based on GPRS or equivalent communication protocol
Local controller for Each Street light
ON / OFF based on CCMS Schedule
Dimming / intensity control based on CCMS Schedule
Should provide Status of ON/OFF and % dimming
Electrical Parameters of Luminaire : Supply voltage, Lamp voltage and current
Lamp and Ballast failure
Switching Point Controller
TO act as local control and remote telemetry unit (RTU)
TO store acquired data of lamp controller and lamp operation of last 20 operational commands
To provide communication link with central control system based on Internet / GPRS.
TO protect information eachange through authorised access controls
Reprogramming capability of the Lamp controller through centralised control system
Switch over facitlity to manual ON/OFF operation mode as programed in case of communication failure
ON and OFF according to the annual calender of sunrise and sunset
Have UPS / battery backup for operation of RTU for smooth operation In power supply loss for minimum 2 hours
Time stamping: For all nodes to be synchronised every day
hardware and its physical location shall be tightly coupled by use of GPS
Data deletion, edition shall not be possible by external device
230V AC, 50Hz, with battery backup for min 2 Hrs
SMF or Lithium Polymer Battery
The telemetry device will be housed in IP 65 enclosure
Door Open Alert on SMS. SMS on movement detection for theft.
Centralized Control & Monitoring System
Following are the key features of CCMS.
Operational Features
• The CCMS unit is capable of switching ON and OFF the lights, Dim light variably as per requirement of a particular light and/or
networked switching points from Central Control Station instantaneously or automatically throughout
the year on basis of Sunrise and sunset time depending on the geographical location of the switching
point.
• The CCMS unit is capable for GPRS and/or GSM/equivalent proven technology based remote
Streetlight monitoring system with capacity for self-protection from short-circuit, over voltage.
• The CCMS Unit is capable requisite Digital Input/output to fetch data.
• Enclosure Box to be Metal enclosure with proper lock arrangement.
Energy measurement as per IS13779 and communication features
• The CCMS unit is capable to capture (record) and provide following parameters at variable timeintervals
(Individual switching point wise and/or networked switching points) :
Voltages
Current
Power Factor
Active Power (kW)
Apparent Power (kVA)
Metering kWh cumulative
Metering kVAh cumulative
• Number of hours the panel was running.
• Special emergency on/off facility with wireless control.
• Generate alert SMS for:
Phase-wise currents on crossing threshold values*
Phase-wise voltages on crossing threshold values*
MCB trips
No output supply
• Alert SMS shall be forwarded to five (5) phone numbers.
Web based Central Control and Monitoring System
• Web-server to receive and record all data from the streetlight controllers.
• It is capable of able to communicate with any individual switching points or collectively amongst
networked switching points for control and monitoring.
• All fault conditions like excess voltage/current drawn, etc through the instantaneous alert messages
sent by the CCMS unit.
• Reports such as energy consumption report, actual hours of operation, etc. is capable of generated on a daily
basis from the data/readings received from the CCMS units.
Different user authorization levels is capable of settable and the central server is capable of capable of
handling high traffic.
• GPS should be installed on each switching point controller and the details of each switch point shall
be viewable in the web application software through a Google-map interface or web based digital map.
CCMS can remotely configured from the Central Control Unit:
• Setting new ON/OFF timings
• Setting the RTC time of Automation unit
• Knowing the current status of any particular switching point.
• Reset the unit.
• The minimum interval for the update of data is capable of 15 minute but programmable up to 1
minute.
• Synchronization of controller with server timing.
CCMS system monitors all the following Points:
• Voltages each phase
• Current each phase
• PF each phase
• Metering KWH cumulative
• Metering KVAH
• Further system is able to indicate various faults
• Failure of contactor
• Overload on the phases
• Each central CCMS unit is capable of handling minimum 250 number switching point units.
• CCMS shall have server preferably dedicated server set-up or cloud based arrangement to ensure
100% guarantee of the data storage for last 3 years
• Data authenticity and validation has to be ensured.
• Cyber security, safe database management, data retrieval and trouble free operation of software and
allied systems (24*7) to be ensured.